## STHAMEX IAF
|  |  | Calibration of Foam Mixer or Emulsifier |  |  |  | STHAMEX IAF |  | 23 of June 2014
|  |  | From the suggestion of Sthamer |  |  |  | http://sthamer.com/englisch/
| Instrument | CDM 80 Conductivity Meter (Radiometer)
Temp set to 19deg C
with 100ml
356 | 0
598 | 1
861 | 2
1063 | 3
4
with 200ml
356 | 0
566 | 1
806 | 2
1055 | 3
Not this serial number
Emulsifier | Conductivity | calc Val
0 | 356 | 0.1038
2 | 498 | 0.7144
3.7 | 753 | 1.8109
4.5 | 995 | 2.8515
6 | 1196 | 3.7158
|  |  |  | Prop % = | 4.3 x 10^-3 x Cond - 1.427 |  | 0.0043
1.427
[microS/cm]
| Real Prop Value = |  | 0.6431 x Reading - 0.2651
|  |  | Reading | 3
0.6631
|  | Calc Value | 1.7242 |  |  | 0.2651
Tabulated Values
|  |  | 0 | -0.2651
|  |  | 1 | 0.398
|  |  | 2 | 1.0611
|  |  | 3 | 1.7242
|  |  | 4 | 2.3873
|  |  | 5 | 3.0504
|  |  | 6 | 3.7135

## Resume
Re |  | Emulsifier Correction for different Foam Agents
| STHAMEX IAF |  |  | Expandol |  | Meteor P Plus
| Emulsifier | Conductivity | calc Val
| 0 | 356 | 0 | Set P Emul | Calculated value | Set point | Simple extrapolation
| 2 | 498 | 0.7144
| 3.7 | 753 | 1.8109 | 0 | -1.0275 | 0 | -3.24
| 4.5 | 995 | 2.8515 | 1 | 0 | 1 | -2.24
| 6 | 1196 | 3.7158 | 2 | 1.0275 | 2 | -1.24
|  |  |  | 3 | 2.055 | 3 | -0.24
|  |  |  | 4 | 3.0825 | 4 | 0.76
|  |  |  | 5 | 4.11 | 5 | 1.76
|  |  |  | 6 | 5.1375 | 6 | 2.76

## EXPANDOL
|  |  | Calibration of Foam Mixer or Emulsifier |  |  |  |  | EXPANDOL |  |  |  | 24 of June 2014
proportion | with 100ml | Calc Value |  |  | Temp set to 19deg C
0 | 354
1 | 617
2 | 850
3 | 1092
| 1362 | 4.1102
|  | Prop % = | 4.1 x 10^-3Cond - 1.4742 |  |  | 0.0041
[6 empty] | 1.474 |  |  |  | 1362 | Set P Emul |  | Calculated value
|  |  | Test at 5% gave a conductivity of |  |  |  | 1362 | [microS/cm] |  |  | 0 |  | -1.0275
[11 empty] | 1 |  | 0
|  |  |  | Calc Prop | 4.1102 | [%] |  |  | Assume 2 values |  | 2 |  | 1.0275
[9 empty] | set points 0 and 5% |  | 3 |  | 2.055
[5 empty] | 1362 | 4.1102 |  |  |  |  | 4 |  | 3.0825
[11 empty] | 5 |  | 4.11
[11 empty] | 6 |  | 5.1375
1.0275
1.0275
Calculated Prop = set P x 1.0275 - 1.0275
[14 empty] | set P | calc P
[14 empty] | 2 | 1.0275

## Meteor P Plus
Metoer P Plus
Temp set to 19deg C
water | 347
Calc Value
with 100ml
347 | 0 | water
906 | 1
1460 | 2
1969 | 3
[11 empty] | Set point | Simple extrapolation
|  |  | Prop % = | 1.84 x 10^-3Cond - 0.658 |  |  | 0.00184
[7 empty] | 0.6586 |  |  |  | 0 | -3.24
[11 empty] | 1 | -2.24
|  |  |  | Test at 5% gave a conductivity of |  |  |  | 1312 | [microS/cm] |  | 2 | -1.24
[11 empty] | 3 | -0.24
[5 empty] | Calc Prop | 1.7555 | [%] |  |  |  | 4 | 0.76
[10 empty] | defined value | 5 | 1.76
[11 empty] | 6 | 2.76
[6 empty] | 1312 | 1.7555

## 23JuneTest01
Foam tests at the CMS Foam Test Centre | [9 empty] | 2014-06-23
Ian Crotty
| Test done with Sthamer personnel ( 2 males, one tall) | [8 empty] | N. Benny
Time | Time | Elapsed time |  | Flow Rate | Flow Meter P | Pump P Gauge | P gauge | P gauge | Foam Agent | State | Foam Height
| Chronometer | [5 empty] | Foam Gen | Foam Gen | Indicated
|  |  | Comments |  |  |  | No Offset |  | proportion
[Hr:min] | [min:sec] | [min:sec] |  | [l/min] | [Bar] | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
#NAME?
15:49 |  |  | water only | 270 |  | 9 |  | 0.12 | 2 | 0 | 0
15;49 |  |  | Foam |  |  |  | 3 | 3.12 | 2 | 1 | 1
15:51 |  | 0 |  | 356 |  |  | 3 | 3.12 | 2 | 1 | 1.5
15:52 | [6 empty] | 3 | 3.12 | 2 | 1 | 2
A bad test, starting conditions not established.
|  |  |  | Foam Agent consummed = |  |  |  | [cm]
|  |  |  | Elapsed time with FA = |  |  |  | [min]
[decimal mins]
Calculated FA proportion from Calibration Curve =

## 23JuneTest02
Foam tests at the CMS Foam Test Centre | [9 empty] | 2014-06-23
Ian Crotty
| Test done with Sthamer personnel ( 2 males, one tall) | [8 empty] | N.Benny
Time | Time | Elapsed time |  | Flow Rate | Flow Meter P | Pump P Gauge | P gauge | P gauge | Foam Agent | State | Foam Height | Temp
| Chronometer | [5 empty] | Foam Gen | Foam Gen | Indicated
|  |  | Comments |  |  |  | No Offset |  | proportion |  |  | Nozzle
[Hr:min] | [min:sec] | [min:sec] |  | [l/min] | [Bar] | [Bar] | [Bar] |  | [%] | [0 or 1] | [m] | [degC]
#NAME?
16:10 |  |  | water only |  |  | 9 |  | 0.12 | 0 | 0 | 0
|  | 0 | Foam turned on |  |  |  | 3 | 3.12 | 6 | 1 | 0
|  | 22s | Foam @ FG | 305 |  |  | 3 | 3.12 | 6 | 1 | 0
16:11 | 16:11 | [5 empty] | 3 | 3.12 | 6 | 1 | 1 | 21.75
| 16:11 | [5 empty] | 3 | 3.12 | 6 |  | 1.5
| 16:12 | [5 empty] | 3 | 3.12 | 6 |  | 2
|  |  |  | Foam Agent consummed = |  |  |  | [cm]
|  |  |  | Elapsed time with FA = |  |  |  | [min]
[decimal mins]
Calculated FA proportion from Calibration Curve =