## Sheet1
Pressure drops in TX/UXC | [5 empty] | Ian Crotty
2014-03-12
Pipe section | Pipe | Dia ID | Length | Flow rate | Fed FGs | speed | Re | Pipe Dp | Bends | Bend Radius | Delta P/Bend | Bend P drop | Hydro-height | Hydrostatic P | Total P loss
| DN | [mm] | [m] | [l/min] |  | [m/s] |  | [mbar] | Quantity | [D] | [mBar] | [mBar] | [m] | [mbar] | [mbar]
[9 empty] | (90deg) | (Long radius)
A-B | DN250 | 260 | 35 | 6000 | 12 | 1.88 | 490000 | 67 | 5 | 1.5 | 4 | 20 | 20 | 2000 | 2087
B-C | DN250 | 260 | 35 | 6000 | 6 | 1.88 | 490000 | 67 | 0 | 1.5 | 4 | 0 | 0 | 0 | 67
C-D | DN250 | 260 | 61.5 | 3000 | 1 | 0.94 | 245000 | 30 | 9 | 1.5 | 4 | 36 | 0 | 0 | 66
X-Y | DN40 | 43 | 10.5 | 500 | 1 | 5.74 | 246000 | 2075 | 4 | 1.5 | 4 | 16 | 5 | 500 | 2591
D-Z | DN40 | 43 | 16.6 | 500 | 1 | 5.74 | 246000 | 3281 | 4 | 1.5 | 4 | 16 | 5 | 500 | 3797
Flow rate total is expected to not exceed 500[l/min/nozzle] see tests done in XXXX
Bends add ~10%/90deg LR bend
Calculating the Individual pressure drop in each section of the "Ring main" is not intersting
as all pesiistic drops are <100mbar and the final line up to the FG is a few bar
FG = Foam generator
[l/min]
|  | Individual flow rates |  | 700
600
500
400
300
200
100
Pipe section | Pipe | Dia ID | Length | Flow rate | Fed FGs | speed | Re | Pipe Dp | Bends | Bend Radius | Delta P/Bend | Bend P drop | Hydro-height | Hydrostatic P | Total P loss
| DN | [mm] | [m] | [l/min] |  | [m/s] |  | [mbar] | Quantity | [D] | [mBar] | [mBar] | [m] | [mbar] | [mbar]
[9 empty] | (90deg) | (Long radius)
A-B | DN250 | 260 | 35 | 6000 | 12 | 1.88 | 490000 | 67 | 5 | 1.5 | 4 | 20 | 20 | 2000 | 2087
A-B | DN250 | 260 | 35 | 4800 | 12 | 1.51 | 391000 | 21 | 5 | 1.5 | 2 | 10 | 20 | 2000 | 2031
A-B | DN250 | 260 | 35 | 3600 | 12 | 1.13 | 294000 | 13 | 5 | 1.5 |  | 0 | 20 | 2000 | 2013
B-C | DN250 | 260 | 35 | 6000 | 6 | 1.88 | 490000 | 67 | 0 | 1.5 | 4 | 0 | 0 | 0 | 67
B-C | DN250 | 260 | 35 | 4800 | 6 |  |  |  | 0 | 1.5
B-C | DN250 | 260 | 35 | 3600 | 6 |  |  |  | 0 | 1.5
C-D | DN250 | 260 | 61.5 | 3000 | 1 | 0.94 | 245000 | 30 | 9 | 1.5 | 4 | 36 | 0 | 0 | 66
X-Y | DN40 | 43 | 10.5 | 500 | 1 | 5.74 | 246000 | 2075 | 4 | 1.5 | 4 | 16 | 5 | 500 | 2591
X-Y | DN50 | 54.5 | 10.5 | 500 | 1 | 3.6 | 194000 | 193 | 4 | 1.5 |  |  | 5 | 500 | 693
D-Z | DN40 | 43 | 16.6 | 500 | 1 | 5.74 | 246000 | 3281 | 4 | 1.5 | 4 | 16 | 5 | 500 | 3797
D-Z | DN40 | 43 | 16.6 | 400 | 1 | 4.59 | 197000 | 2100 | 4 | 1.5 | 4 | 16 | 5 | 500 | 2616
D-Z | DN40 | 43 | 16.6 | 300 | 1 | 3.44 | 148000 | 1184 | 4 | 1.5 | 4 | 16 | 5 | 500 | 1700
D-Z | DN50 | 54.5 | 16.6 | 500 | 1 | 3.6 | 194000 | 306 | 4 | 1.5 |  |  | 5 | 500 | 806