## June11
Foam tests at the CMS Foam Test Centre | [8 empty] | 2014-06-11
Ian Crotty
Time | Elapsed time |  | Flow Rate | Flow Meter P | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height
[6 empty] | Foam Gen | Foam Gen
|  | Comments |  |  |  | Off set |  | proportion
State
| [min:sec] |  | [l/min] | [Bar] | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
17:15 |  | water only | 316 | 7.6 | 7.5 | 3.3 | 3.42 | 0 | 0
17:17 |  | water only | 320 |  |  |  |  | 0 | 0
17:19
| 1:20 | [6 empty] | 1 | 1
| 1:40 |  |  |  | 7.5 | 3.3 |  | 2 | 1
17:20 | 3:15 | Wind, foam over flow |  |  |  | 3.3 |  | 3 | 1
17:24 | 7:00 | 0.5m from top | [7 empty] | 3.5
17:25 | 8:00 | Foam Over flow | [7 empty] | 4
Waves
17:28 |  | Foam Elimination
17:45 |  | 1/4 foam left | [7 empty] | 1 | Kink in hose to FG
17:47 |  | almost gone | [7 empty] | 0.25

## 12June1Bar
2014-06-12
| Foam tests at the CMS Foam Test Centre | [5 empty] | FG = Foam Generator |  |  |  |  | 2014-06-12
Ian Crotty
| Time | Time | Elapsed time |  | Flow Rate | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height
|  | Chronometer | [6 empty] | Foam Gen | Foam Gen
|  |  |  | Comments |  |  |  |  | Off set |  | proportion
State
| [Hr:min] | [min:sec] | [min:sec] |  | [l/min] | [Bar] |  | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
| 15:36 |  |  | water only | 187 | 3 |  | 4.5 | 1 | 1.12 | 0 | 0 | 0
190
| 15:37 | 0:00 | 0 | Start Foam |  | 3 |  | 4.5 | 1 | 1.12 | 3 | 1 | 0
|  |  | 0:21 | foam at FG
| 15:43 | 3:18 | 2:57 | [9 empty] | 1
|  | 5:03 | 1:45 | [7 empty] | 0 | 0 | 1.5
15:45
| 15:50 | [11 empty] | 0.2
FA consummption not taken
Cleaning with x2 lances

## DrumCapacity
Blue plastic drum
3.1416
Dia = | 57 | cm | Not really cylindrical !!
Height = | 90 | cm
Calculated Vol |  | 229.6581 | [litres]
Real Vol is 200 Litres ? Suspect the dia estimation is not so good. Also the height to full is more like 85
Height | 85 | cm
Calc Vol = |  | 216.8993 | [litres]
With dia | 55 | cm
Cal vol = |  | 201.9453 | [litres]
Within 1% we have the barrel dimensions Containing fluid(ie liquid vol!)
Drum dia = | 55
Height | 85
Therfor we can calculate a vol as a function of height. Namely Vol/unit height [litres/cm]
| In this blue plastic drum case Vol/unit height |  |  |  | 2.3758 | [l/cm]

## 12June2Bar
Foam tests at the CMS Foam Test Centre | [5 empty] | FG = Foam Generator |  |  |  |  | 2014-06-12
Ian Crotty
Time | Time | Elapsed time |  | Flow Rate | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height
| Chronometer | [6 empty] | Foam Gen | Foam Gen
|  |  | Comments |  |  |  |  | Off set |  | proportion
State
[Hr:min] | [min:sec] | [min:sec] |  | [l/min] | [Bar] |  | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
15:58 |  |  | water only | 250 | 5.25 |  | 5 | 2 | 2.12 | 0 | 0 | 0.1
[8 empty] | 1.9 | 2.02
15:59 |  |  |  | 249 | 5.25 |  | 4.95 | 2 | 2.12 | 0 | 1
16:00 |  | 0 | Foam on | 235 | [5 empty] | 3 | 1 | 0.1
|  | 14 | Foam appears | 241 | [7 empty] | 0.1
|  | 1:12 |  | 239 | [7 empty] | 1
16:02 |  | 0:34 | [9 empty] | 1.5
|  |  | Foam off | [6 empty] | 0 | 0 | 1.5
|  | 0:15 | no more foam FG | 0 | [5 empty] | 0 | 0
16:07 |  |  | Removing Foam | [8 empty] | 1.5
16:13 |  |  | Stopped | [8 empty] | 0.15

## Resume
[7 empty] | Test 11 - 24 June 2014 | [6 empty] | Ian Crotty
Resume
| Date |  | Foam | P @ FG | Proportion H2O/FA | Time run | Flow rate | Water | FA Consummed | Foam Height | Foam Vol | Foam Rate |  | Expansion Ratio | Smoke | Weight burnt | Shrouds FG |  |  | Foam Ratios |  |  |  | Kidi Specification |  |  |  |  | Calculated flow rates for dia 5mm nozzle
|  |  | Type |  |  | Water+FA | water | [7 empty] | 0/1 | [13 empty] | http://irrigation.wsu.edu/Content/Calculators/Sprinkler/Nozzle-Requirements.php
[7 empty] | Reading |  | 2.38[l/cm] | [10 empty] | Pressure | Nozzles | Water quantity |  | Foam Quantity |  | Foam Agent |  |  |  | Inlet Pressure | Flow RTE | Flow rate for 9 Nozzles
[9 empty] | 2.38 | [10 empty] | [Bar] |  | [l/min] |  | [m3/min] | [m3/min] | [litres/min] |  |  |  | [Bar] | [l/min]
|  |  |  | [Bar] | [%] | [min] | [l/min] | [litres] | [litres] | [m] | [m3] | [m3/min] | [m3/min] |  |  |  | state | FA Ratio [%] | 3 |  |  |  |  | 9 nozzles | 1 nozzle
[12 empty] | 9 nozzles | 1 nozzle |  |  |  |  | Expansion Ratio | 720 | 4 | 9 | 270 |  | 194.4 | 21.6 | 8.1 |  |  |  | 0 | 0 | 0
|  |  | Drum P5 | 1.12 | 3 | 4.7 | 188.5 | 885.95 | ? | 1.5 | 164.475 | 34.9947 | 3.8883 | 185.6482 | 0 | [5 empty] | 1 | 30 |  | 0 | 0 | 0.9 |  |  |  | 0.5 | 11.4 | 102.6
|  |  | Drum P5 | 2.12 | 3 | 1.75 | 240 | 420 | ? | 1.4 | 153.51 | 87.72 | 9.7467 | 365.5 | 0 | [8 empty] | 0 | 0 | 0 |  |  |  | 1 | 16.2 | 145.8
|  |  | Drum P5 | 3.12 | 3 | 2.02 | 310 | 626.2 | 9.996 | 1.4 | 153.51 | 75.995 | 8.4439 | 245.1453 | 0 |  |  |  | 810 | 6 | 9 | 340 |  | 275.4 | 30.6 | 10.2 |  |  |  | 2 | 22.9 | 206.1
|  | Test01 | Drum P5 | 3.92 | 3 |  | 445 | 0 |  | 0 | No Foam |  |  |  | 0 | [5 empty] | 1 | 37.7778 |  |  | 0 |  |  |  |  | 3 | 28 | 252
|  | Test02 | Drum P5 | 4.02 | 3 | 4.37 | 370 | 1616.9 |  | 1.5 | 164.475 | 37.6373 | 4.1819 | 101.7224 | 0 | [14 empty] | 4 | 32.3 | 290.7
|  | Test03 | Drum P5 | 4 | 3 | 5.92 | 370 | 2190.4 |  | 1.5 | 164.475 | 27.7829 | 3.087 | 75.089 | 1 | [14 empty] | 5 | 36.1 | 324.9
|  | Test04a | Drum P5 | 6.12 | 3 | 2.52 | 425 | 1071 | 26.66 | 1.5 | 164.475 | 65.2679 | 7.252 | 153.5714 | 0 | [7 empty] | 9nozzles | 1 nozzle | [5 empty] | 6 | 39.6 | 356.4
|  | Test04b | Drum P5 | 3.02 | 3 | 5.6 | 320 | 1792 | 31.42 | 1.5 | 164.475 | 29.3705 | 3.2634 | 91.7829 | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 7 | 42.8 | 385.2
| 2014-06-23 | test 01a | Sthamex IAF | 3.12 | 2 | 3.05 | 356 | 1085.8 | ? | 2 | 219.3 | 71.9016 | 7.9891 | 201.9709 | 0 |  | 1 |  |  | 4 | 270 | 720 | 194.4 | 21.6 | [5 empty] | 8 | 45.7 | 411.3
| 2014-06-23 | test01b | Sthamex IAF | 3.12 | 6 | 2.75 | 356 | 979 | ? | 2 | 219.3 | 79.7455 | 8.8606 | 224.0041 | 0 |  | 1 |  |  | 6 | 340 | 810 | 275.4 | 30.6 | [5 empty] | 9 | 48.5 | 436.5
| 2014-06-23 | Test01c | Sthamex IAF | 3.12 | 4.5 | 2.33 | 356 | 829.48 | ? | 1.5 | 164.475 | 70.5901 | 7.8433 | 198.2869 | 0 |  | 1 | [12 empty] | 10 | 51.1 | 459.9
[18 empty] | SCUM | [11 empty] | 11 | 53.6 | 482.4
[25 empty] | The scale on this company plot is poor !! |  |  |  |  | 12 | 56 | 504
|  |  | Drum P5 = SINTO K4S | [22 empty] | Pressure | Foam Rate | Flow Rate
FG = Foam generator
|  |  | FA = Foam Agent | [22 empty] | [Bar] | [m3/min] | [l/min]
[26 empty] | 0 | 0 | 0
[26 empty] | 4.8 | 12
[26 empty] | 5 | 15.2 | 27.5
[26 empty] | 6 | 18 | 30
[26 empty] | 7 | 17.8 | 32.7
[26 empty] | 7.5 | 17 | 33.5
[18 empty] | Conductivity |  | Prop set P. |  | Real Prop
[20 empty] | 0 |  | 0
[18 empty] | 498 |  | 2 |  | 0.623
[18 empty] | 995 |  | 4.5 |  | 2.736
[18 empty] | 1200 |  | 6 |  | 3.61
Calc. prop. = 0.7768 x Set Point - 0.8303
[19 empty] | Set Point Reading |  | 2.5
[19 empty] | Calc Proportion |  | 1.1117
[14 empty] | Set point | Real Ratio
[14 empty] | 1 | -0.1552
[14 empty] | 2 | 0.5934
[14 empty] | 3 | 1.342
[14 empty] | 4 | 2.0906
[14 empty] | 5 | 2.8392
[14 empty] | 6 | 3.5878
[14 empty] | 7 | 4.3364

## 12June3Bar
Foam tests at the CMS Foam Test Centre | [5 empty] | FG = Foam Generator |  |  |  |  | 2014-06-12
Ian Crotty
Time | Time | Elapsed time |  | Flow Rate | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height
| Chronometer | [6 empty] | Foam Gen | Foam Gen
|  |  | Comments |  |  |  |  | Off set |  | proportion
State
[Hr:min] | [min:sec] | [min:sec] |  | [l/min] | [Bar] |  | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
16:22 |  |  | water only | 310 | 7.6 |  | 7.2 | 3 | 3.12 | 0 | 0 | 0.1
0.12
16:32 |  |  |  | 310 |  |  |  | 2.95 | 3.07 | 3 | 0 | 0.1
16:33 |  | 0 |  | 310 |  |  |  | 2.95 | 3.07 | 3 | 1
|  | 0:11 | time for foam to FG |  |  |  | 7.2 |  |  | 3 | 1
|  | 1:16 | [9 empty] | 1
0:45
0:18
16:35 |  |  | Foam stopped | [9 empty] | m
|  |  |  | Foam Agent consummed = |  | 4.2 | [cm]
|  |  |  | Elapsed time with FA = |  | 2:01 | [min]
[6 empty] | 2.02 | [decimal mins]

## Test0120June2014
Foam tests at the CMS Foam Test Centre | [5 empty] | FG = Foam Generator |  |  |  |  | 2014-06-20
Test No 1 | [10 empty] | Ian Crotty
Time | Time | Elapsed time |  | Flow Rate | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height
| Chronometer | [6 empty] | Foam Gen | Foam Gen
|  |  | Comments |  |  |  |  | Off set |  | proportion
State
[Hr:min] | [min:sec] | [min:sec] |  | [l/min] | [Bar] |  | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
15:16 |  |  | water only | 490 |  |  | 5.9 |  | 0.12 | 0 | 0 | 0.1
0.12
15:18 |  |  |  | 490 |  |  | 5.9 |  | 0.12 | 3 | 1 | 0.1
15:20 |  | 0 | Fails no Foam | 440 | 9.95 |  | 9.8 | 3.8 | 3.92 | 3 | 1
15:24 |  |  | F Rate + - 10% | 445 | 9.8 |  | 9.8 | 3.8 | 3.92 | 3 | 1 | 3.7 | ??
15:26 |  |  | Off | [5 empty] | 0.12
0.12
0.12
0.12
| 5.2 [m/s] |  |  | Foam Agent consummed = |  |  | [cm] |  | P gauge Flow meter Off set of -0.4Bar at "0" Bar
|  |  |  | Elapsed time with FA = |  |  | [min]
[decimal mins]

## Test0220June2014
| Foam tests at the CMS Foam Test Centre | [5 empty] | FG = Foam Generator |  |  |  |  | 2014-06-20
| Test No 2 | [10 empty] | Ian Crotty
| Time | Time | Elapsed time |  | Flow Rate | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height
|  | Chronometer | [6 empty] | Foam Gen | Foam Gen
|  |  |  | Comments |  |  |  |  | Off set |  | proportion
State
| [Hr:min] | [min:sec] | [min:sec] |  | [l/min] | [Bar] |  | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
| 15:26 |  |  | Previous test stopped | [6 empty] | 0 | 0 | 0
0.12
| 15:45 |  |  |  | 360 |  |  |  | 3.9 | 4.02 | 0 | 0
| 15:47 |  |  |  | 360 |  |  |  | 3.9 | 4.02 | 0 | 0
| 15:48 | [6 empty] | 9.9 | 3.8 | 3.92 | 3 | 1
|  | 0:00 | [8 empty] | 3 | 1
|  | 0:09 | 0:00 | Foam starts Good Foam | [6 empty] | 3 | 1 | 0
|  | 2:56 | 2:47 | [9 empty] | 1
|  | 4:31 | 4:22 | [9 empty] | 1.5
| 15:50 |  |  |  | 370 | [5 empty] | 3 | 1
| 15:52 |  |  | Stop | [6 empty] | 0 | 0
|  | Air Speed FA | [5 empty] | Next test is with smoke starts at 16:19
[m/s]
|  | Side FG | 4 |  | Foam Agent consummed = |  | unnknown | [cm] |  | P gauge Flow meter Off set of -0.4Bar at "0" Bar
|  | middle FG | 4.6
|  | Centre | 4.2 |  | Elapsed time with FA = |  | 4:22 | [min]
[7 empty] | 4.37 | [decimal mins]
Foam Generator
Side
Centre
Middle ?

## Test0320June2014
Foam tests at the CMS Foam Test Centre | [6 empty] | FG = Foam Generator |  |  |  |  | 2014-06-20
Test No 3 |  |  |  |  | With Smoke | [6 empty] | Ian Crotty
Time | Time | Elapsed time |  | Flow Rate |  | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height
| Chronometer | [7 empty] | Foam Gen | Foam Gen
|  |  | Comments | [5 empty] | Off set |  | proportion
State
[Hr:min] | [min:sec] | [min:sec] |  | [l/min] | ± | [Bar] | ± | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
15:52 |  |  | Previous test stopped | [7 empty] | 0 | 0 | 0
0.12
16:20 |  |  | Fire on | 370 | 5 |  |  | 9.8 | 3.9 | 4.02 | 3 | 0
16:22 |  |  |  | 370 |  |  |  |  | 3.9 | 4.02 | 3 | 0
16:24 | [7 empty] | 9.9 | 3.8 | 3.92 | 3 | 1
| 0:00 | [9 empty] | 3 | 1
| 0:08 |  | Foam starts | [7 empty] | 3 | 1 | 0
| 4:17 | 4:09 | [10 empty] | 1
| 1:46 | [11 empty] | 1.5
|  |  |  | 370 | [6 empty] | 3 | 1
16:29 |  |  | Stop | [7 empty] | 0 | 0
Air Speed FA
[m/s]
| Side FG |  |  | Foam Agent consummed = |  |  | 20.4 | [cm] |  | P gauge Flow meter Off set of -0.4Bar at "0" Bar
| middle FG | [5 empty] | 48.552 | [litres]
Centre
|  |  |  | Elapsed time with FA = |  |  | 5:55 | [min]
[7 empty] | 5.92 | [decimal mins]
32degC
230degC @ 2m above fire base
150degC

## Test0420June2014
| Foam tests at the CMS Foam Test Centre | [6 empty] | FG = Foam Generator |  |  |  |  | 2014-06-20
| Test No 4 |  |  |  |  | With Smoke & with out | [6 empty] | Ian Crotty
| Time | Time | Elapsed time |  | Flow Rate |  | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height
|  | Chronometer | [7 empty] | Foam Gen | Foam Gen
|  |  |  | Comments | [5 empty] | Off set |  | proportion
State
| [Hr:min] | [min:sec] | [min:sec] |  | [l/min] | ± | [Bar] | ± | [Bar] | [Bar] |  | [%] | [0 or 1] | [m]
| 16:29 |  |  | Previous test stopped | [7 empty] | 0 | 0 | 0
0.12
| 17:26 |  |  | No Fire | 420 | 10 |  |  | 13.9 | 6 | 6.12 | 3 | 0
|  | 0:10 |  | Start Foam | [7 empty] | 3 | 1 | 0
|  | 4:20 |  | stop | [7 empty] | 3 | 1 | 0.2
[12 empty] | 0 | 0 |  | Foam Agent consummed = | 11.2 | [cm]
Test 4a | 17:28 | [10 empty] | 3 | 0 |  |  | 26.656 | [litres]
| 17:31 |  |  |  | 425 |  |  |  | 14 | 6 | 6.12 | 3 | 1
| 17:32 |  |  | off, water still on | 425 | [6 empty] | 0 | 0
| 17:35 |  |  |  | 320 | 10 |  |  | 7.9 | 3.2 | 3.32 | 0 | 0 |  | Elapsed time with FA = | 2:31 | [min]
|  | 0:08 |  | Start Foam | [11 empty] | 2.5167 | [decimal mins]
|  | 1:39 | 1:31 | Good Foam | [9 empty] | 1
|  | 1:00 | 2:31 | Massive bubbles >10cm | [9 empty] | 1.5
| 17:37 |  |  | Foam off | [7 empty] | 0 | 0
| 17:38 |  |  | Stop
| 17:39 |  |  | Water off
| 17:55 |  |  | Smoke on | 320 | 10 |  |  | 8 | 2.9 | 3.02 |  |  |  | Foam Agent consummed = | 13.2 | [cm]
| 17:57 |  |  | Water on | [6 empty] | 0.12 |  |  |  |  | 31.416 | [litres]
Test 4b |  | 0:13 |  | Foam on | [6 empty] | 0.12 | 3 | 1 | 0
|  | 3:42 | 3:29 | [7 empty] | 0.12 |  |  | 1
|  | 2:07 | 5:36 | [7 empty] | 0.12 |  |  | 1.5 | Elapsed time with FA = | 5:36 | [min]
| 18:00 |  |  |  | 325 | 5 |  |  |  |  | 0.12 |  |  |  |  | 5.6 | [decimal mins]
0.12

## Test0123June2104
Sthamex IAF
| Foam tests at the CMS Foam Test Centre | [6 empty] | FG = Foam Generator |  |  |  |  | 2014-06-23 | [6 empty] | Condictivity meter | [5 empty] | lenntech.com
| Test No 1 |  |  |  |  | With No Smoke | [6 empty] | Ian Crotty | [8 empty] | [microS/cm] | [5 empty] | [S/m]
|  |  | Elapsed time | [17 empty] | water | 200 | 300 |  |  | Ultra pure water |  | 5.5e-06
| Time | Time |  |  | Flow Rate |  | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height | Measured | Temp | [9 empty] | Drinking water |  | 0.005
|  | Chronometer | [7 empty] | Foam Gen | Foam Gen |  |  |  | Prop. | [10 empty] | Drinking water |  | 0.05
|  |  |  | Comments | [5 empty] | Off set |  | proportion
[13 empty] | State | [6 empty] | CDM Conductivity Meter (Radio Meter Copenhagen)
| [Hr:min] | [min:sec] | [min:sec] |  | [l/min] | ± | [Bar] | ± | [Bar] | [Bar] |  | [%] | [0 or 1] | [m] | [%] | [degC
[21 empty] | Conductivity | temp [degC] | Stharmex IAF | Weight | Weight | Vol mreasured
[23 empty] | Proportion | H2O | FA
| 15:49 | [10 empty] | 0 | 0 | 0 | [6 empty] | [microS/cm] |  | [%] | [g] | [g] | [mL]
No Fire
| 15:49 | [19 empty] | 356 | 25 | 0 |  |  |  |  | Tap water
|  |  |  | No Foam | 270 | 10 |  |  | 9 |  |  | 2 | 1 | 0 | 0.623 |  | Foam Agent consummed = | ? | [cm] |  | 861 |  | 2 |  |  | 100
| 15:50 |  |  | Start Foam | 356 | 10 |  |  |  | 3 | 3.12 | 2 | 1 | 0 | 0.623 |  |  |  | [litres] |  | 0 | [6 empty] | Air
| 15:49 | 0:00 |  | 498 [microS/cm] | 356 | 10 |  |  |  | 3 | 3.12 | 2 |  | 1 | 0.623 | [5 empty] | 598 |  | 1 |  |  | 100
| 15:51 | 2:38 |  |  | 356 | 10 |  |  |  | 3 | 3.12 | 2 |  | 1.5 | 0.623 |  | Elapsed time with FA = | 3:03 | [min] |  | 1063 |  | 3 |  |  | 100
| 15:52 | 3:03 |  |  | 356 | 10 | [5 empty] | 2 |  | 2 | 0.623 |  |  | 3.05 | [decimal mins]
[21 empty] | 356 |  | 0 |  |  |  |  | Air
| 16:10 |  |  | 1200 [microS/cm] | [12 empty] | Foam Agent consummed = | ? | [cm] |  | 567 |  | 1 | 198.6 | 2.001
|  | 0:00 |  | Start | 305 | 10 |  |  | ? | 3 | 3.12 | 6 | 0 | 0 | 3.61 | 21.75 |  |  | [litres] |  | 806.5 |  | 2 | 196 | 4.02
|  | 0:22 |  | Foam starts | [5 empty] | 3 | 3.12 | 6 | 1 | 1 | 3.61 | [5 empty] | 1055 |  | 3 | 194 | 6.02
|  | 1:19 |  | Good Foam | [5 empty] | 3 | 3.12 | 6 | 1 | 1.5 | 3.61 |  | Elapsed time with FA = | 2:45 | [min]
|  | 1:45 | 2:45 | [6 empty] | 3 | 3.12 | 6 | 1 | 2 | 3.61 |  |  | 2.75 | [decimal mins]
| 16:12 |  |  | Stop
Water off
0.12
| 16:42 |  |  | 995 [microS/cm] | [5 empty] | 3 | 3.12 | 4.5 |  |  | 2.736 | 28
|  | 0:20 |  | Water on | [5 empty] | 3 | 3.12 | 4.5 |  | 0 | 2.736
|  |  |  | Foam on | [5 empty] | 3 | 3.12 | 4.5 | 1 | 0 | 2.736 |  | Elapsed time with FA = | 2:20 | [min]
|  | 1:45 |  | Foam on | [5 empty] | 3 | 3.12 | 4.5 |  | 1 | 2.736 |  |  | 2.3333 | [decimal mins]
|  | 2:40 | 2:20 | Foam on | [5 empty] | 3 | 3.12 | 4.5 |  | 1.5 | 2.736
| 17:35 |  |  | Fire on | [5 empty] | 3 | 3.12 | 4 | 0 | 0.2 | 1.708 |  | Fire on at 16:58
753 [micro S./cm] | 17:46 | 0:05 |  | Start water & FA | 313 | 10 |  |  | 8.2 | 3 | 3.12 | 4 |  | 0.2
|  | 0:10 |  | Foam | [5 empty] | 3 | 3.12 |  |  | 0.2
|  | 1:17 | [7 empty] | 3 | 3.12 |  |  | 1
|  | 2:07 | [7 empty] | 3 | 3.12 |  |  | 1.5
|  | 3:09 | [7 empty] | 3 | 3.12 |  |  | 2
|  | Air Speeds in Chimney @ 1.3m above base |  |  |  |  | Conductivity |  | Prop set P. | Real Prop
[27 empty] | Conductivity = |  | 753 | [micro Sivert]
| FG | Doors open | 1.5 - 2.0 | [m/s] | [17 empty] | Trial 2 | Proportion = 0.0042 x Conduct - 1.5102 |  |  |  |  | Proportion | 1.7075 | [%]
| FG | Doors shut | 3.7- 4.3 | [m/s] |  |  |  |  | 0 | 0
[7 empty] | 498 |  | 2 | 0.6833 | [12 empty] | Therefore Calc. Water = 360 [micro Siverts/cm]
[7 empty] | 753 |  | 4 | 1.7075
[7 empty] | 995 |  | 4.5 | 2.736 | [11 empty] | Trial 1 | Proportion = 0.0043 x Conduct - 1.4753
[7 empty] | 1200 |  | 6 | 3.61
[7 empty] | Calc. prop. = 0.7486 x Set Point - 0.9038 | [15 empty] | Therefore Calc. Water = 343 [micro Siverts/cm]
[7 empty] | Set Point Reading |  | 5
[7 empty] | Calc Proportion |  | 2.8392
See aslo measurements from;
"Test2324June2014Sthamer"
http://rpc-cms-re4-upscope.web.cern.ch/rpc-cms-re4-upscope/RPC/Safety/CMS%20Foam/Tests/23June2014/Test2324June2014Sthamer.xlsx
Temperatures in the smoke generator
| Data form; |  |  | Time |  | FB2m | Horiz | BoxFG
| Noemi & Zoltan |  |  | [hh:mm:ss] |  | [degC] | [degC] | [degC]
|  |  |  | 17:42:?? |  | 180 | 148 | 68
|  |  |  | 17:45:?? |  | 316 | 255 | 105
|  |  |  | 17:46 |  | 316 | 255 | 105
|  |  |  | 17:46 |  | 281 | 207 | 97
|  |  |  | 17:47 |  | 234 | 163 | 34
|  |  |  | 17:47 |  | 246 | 160 | 34
|  |  |  | 17:48 |  | 239 | 145 | 33
|  |  |  | 17:49 |  | 202 | 132 | 31
|  |  |  | 17:50 |  | 197 | 133 | 32
FB2m = 2m above the fire box base
Horiz = position in the horizontal portion just before the FG
BoxFG = position in the shrowd infron of the FG
FG = Foam Generator

## Test0124June2014
Test
Expandol
| Foam tests at the CMS Foam Test Centre | [6 empty] | FG = Foam Generator |  |  |  |  | 2014-06-24 | [6 empty] | Condictivity meter
| Test No 1 |  |  |  |  | With Smoke | [6 empty] | Ian Crotty
|  |  | Elapsed time | [16 empty] | Expandol
| Time | Time |  |  | Flow Rate |  | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height | Measured | Temp |  |  |  | Conductivity = 1358 - 1362 microS/cm
|  | Chronometer | [7 empty] | Foam Gen | Foam Gen |  |  |  | Prop.
|  |  |  | Comments | [5 empty] | Off set |  | proportion
[13 empty] | State | [6 empty] | CDM Conductivity Meter (Radio Meter Copenhagen)
| [Hr:min] | [min:sec] | [min:sec] |  | [l/min] | ± | [Bar] | ± | [Bar] | [Bar] | [Bar] | [%] | [0 or 1] | [m] | [%] | [degC
[21 empty] | Conductivity = |  | 1362 | [micro Sivert]
| Smoke is formed by burning 1/4 small motor bike tyre | [20 empty] | Proportion | 4.0827 | [%]
| 10:20 |  | 0:00 | No Fire | 320 | 10 |  |  |  | 3 | 3.12 | 5 | 0 | 0 | 4.08
| 10:22 |  | 0:02 | [7 empty] | 0.12 |  | 1 | 1.5
| 10:23 |  | 0:03 | [7 empty] | 0.12 |  | 1 | 2
| 10:24 |  | 0:04 | [9 empty] | 1 | 2.5 |  |  | Foam Agent consummed = | ? | [cm]
| 10:25 |  |  | Stop | [8 empty] | 0 | [5 empty] | [litres]
[17 empty] | Elapsed time with FA = | 4:00 | [min]
[18 empty] | 4 | [decimal mins]
Meteor P Plus
| Foam tests at the CMS Foam Test Centre | [6 empty] | FG = Foam Generator |  |  |  |  | 2014-06-24 | [6 empty] | Condictivity meter
| Test No 2 |  |  |  |  | With Smoke | [6 empty] | Ian Crotty
|  |  | Elapsed time | [16 empty] | Expandol
| Time | Time |  |  | Flow Rate |  | Flow Meter P |  | Pump P Gauge | P gauge | P gauge | Foam Agent |  | Foam Height | Measured | Temp |  |  |  | Conductivity = 1358 - 1362 microS/cm
|  | Chronometer | [7 empty] | Foam Gen | Foam Gen |  |  |  | Prop.
|  |  |  | Comments | [5 empty] | Off set |  | proportion
[13 empty] | State | [6 empty] | CDM Conductivity Meter (Radio Meter Copenhagen)
| [Hr:min] | [min:sec] | [min:sec] |  | [l/min] | ± | [Bar] | ± | [Bar] | [Bar] | [Bar] | [%] | [0 or 1] | [m] | [%] | [degC
[21 empty] | Conductivity = |  | 1312 | [micro Sivert]
| Smoke is formed by burning 1/4 small motor bike tyre + 2.3kg of Cables + 4.15kg Wood | [20 empty] | Proportion | 3.8787 | [%]
| 11:28 | 0:00 |  | No Fire | 320 | 10 |  |  | 7.9 | 3 | 3.12 | 4 | 0 | 0.2
[10 empty] | 3 | 3.12 |  | 1 | 1
| 11:33 | 0:05 |  | Time 11:33?? | [5 empty] | 3 | 3.12 |  | 1 | 1.5
[10 empty] | 3 | 3.12 |  | 1 | 2 |  |  | Foam Agent consummed = | ? | [cm]
| 11:37 | 0:09 | [7 empty] | 3 | 3.12 |  | 1 | 2.5 |  |  |  |  | [litres]
| 11:39 | 0:11 | [7 empty] | 3 | 3.12 |  | 1 | 3
|  |  |  | Stop | [12 empty] | Elapsed time with FA = |  | [min]
[decimal mins]
http://rpc-cms-re4-upscope.web.cern.ch/rpc-cms-re4-upscope/RPC/Safety/CMS%20Foam/Tests/23June2014/Test2324June2014Sthamer.xlsx
Metoer P Plus

## Conclusions
Conclusions
take time to take data and ensure that all parameters are covered/recorde both before and after.
Do a smaller scale with better foam height measurement/Vol
The flow rate as made by the Fire Brigade flow meter appears to be optimistic see plot