## Slide 1: Foam Test Some initial analysis
Ian Crotty 2 March 2015

## Slide 2: Initial Tests in new Foam Bunker
Tests done with
      Santo K 4S ( old stock from P5)
      Sthamex
      Expandol
      MeteorP Plus
Foam Generator Kidde HEFG 35 and Smoke/heat source

## Slide 3: Pressure versus flow rate
The calc. nozzle and the Kidde spec agree but the measurements do not indicating an optimistic flow meter or low “P” reading.

## Slide 4: Foam Production versus inlet Pressure
From a SCUM HG 15 there is a maximium in the Foam rate
The two specified operating points from Kidde are far above the test data. Results for 1 nozzle.
Chart: Foam Production Rate
| 3.8882978723404258 | 9.7466666666666661 | 8.4438943894389435 | 4.1819221967963394 | 7.2519841269841283
Old DrumP5 | 1.12 | 2.12 | 3.12 | 4.02 | 6.12
HG-15 | 4.8 | 5 | 6 | 7 | 7.5
Kidde | 4 | 6

## Slide 5: Expansion ration & Flow rate
Expansion ratio is far below spec. Smoke makes thing worse.

## Slide 6: Conductivity to define proportion
Chart: Conductivity of H2O/Foam Agent
| 356 | 598 | 861 | 1063
100ml | 0 | 1 | 2 | 3
200ml | 0 | 1 | 2 | 3

## Slide 7: Mixture ratio off set
The real proportion is made from electrical conductivity of the mixed solution.

## Slide 8: Eductor corrections for different Foam Agents
Chart: 
| 0 | 2 | 3.7 | 4.5 | 6
Sthamex IAF | 0 | 0.7144 | 1.8109 | 2.8515 | 3.7158
Expandol | -1.0275 | 0 | 1.0275 | 2.055 | 3.0825 | 4.11 | 5.1375
MeteorP Plus | -3.24 | -2.24 | -1.24 | -0.24 | 0.76 | 1.76 | 2.76
This plot is not done with a serious method

## Slide 9: Smoke & Temperature test measurements
Temperatures and air flow speeds were recorded.
Temperatures in the smoke generator |  |  |  | 
Time |  | FB2m | Horiz | BoxFG
[hh:mm:ss] |  | [degC] | [degC] | [degC]
17:42:?? |  | 180 | 148 | 68
17:45:?? |  | 316 | 255 | 105
17:46:05 |  | 316 | 255 | 105
17:46:10 |  | 281 | 207 | 97
17:46:31 |  | 234 | 163 | 34
17:46:52 |  | 246 | 160 | 34
17:48:18 |  | 239 | 145 | 33
17:49:07 |  | 202 | 132 | 31
17:49:32 |  | 197 | 133 | 32
FB2m = 2m above the fire box base |  |  |  | 
Horiz = position in the horizontal portion just before the FG |  |  |  | 
BoxFG = position in the shrowd infron of the FG |  |  |  | 
FG = Foam Generator |  |  |  | 
Data from;
Noemi & Zoltan
Side
Smoke box entry to Foam Generator

## Slide 10: Conclusions
The time must be taken that all parameters are/ have been taken befor4e moving on to the next. Data points have been lost and are far from credible as essential values are not recorded.
Do smaller scale with better foam height evaluation and correct dainage.
The flow rate given by the Fire brigade flow meter appears optimistic.
So far we have not seen any sign of a maxima in the foam rate.
Smoke and or heat appears to reduce significantly the foam production.
But we have no reliable values.
The method of mixing is not reliable across different Foam Agents and perhaps not across the flow rates we were using.

## Slide 11
How it started
June 2014

## Slide 12: Fire Brigade eductor and flow meter

## Slide 13: Bunker location on CERN site
Has been modified since this aerial image was taken