## Slide 1: GIF
Proposition de porte blindée coulissante interlockée
https://edms.cern.ch/document/1729102/

## Slide 2
Poutres acier 3222
Permanent shielding
1.6 m
2.4 m
Concrete Pillar
Concrete Pillar

## Slide 3
Poutres acier
Steel structure + rail
1.6 m
2.4 m

## Slide 4
Poutres acier
Steel structure + rail
Shielded door (Lxhxl)
1.8x2.5x0.1m³
(3.5t )

## Slide 5
Poutres acier
Steel structure + rail
Shielded door (Lxhxl)
1.8x2.5x0.1m³
(3.5t )

## Slide 6: GIF Porte blindée coulisante
Cost estimate:
Item | Cost [KCHF]
Steel structure | 10
Rails + sliders | 3
Door steel plate 3.5t | 10
Steel floor modification | 2
Furnitures | 2
Access cabling | 3
TOT | 30
This door is operated by hand (no motor), effort < 150N, aperture time < 20s
Max 4 hours to remove the door, steel structures + concrete blocks in case a large aperture is needed. (or 2 hours for roof opening)

## Slide 7: GIF Porte blindée coulisante
To be validated by RP:
Thickness of this door (steel S235, 100mm ?)
Overlap 100 mm on sides and on top with max 10 mm gap
Gap max 10 mm to floor
In case of intrusion time respond for the source to be off

## Slide 8: AWAKE shielded door design

## Slide 9: Design porte AWAKE
Dimensions:
2.2x1.4x0.1 m³
Mass: 2400 kg
Gap above floor: 10mm
Stroke: 1.4m

## Slide 10: Design porte AWAKE
Free clearance:
Lxh = 1.2x2m²
The doors are operated by hand
Effort < 100N
Aperture time < 10s
(A spring or a counterweight can be added for assistance if needed)

## Slide 11
ST0746517
ST0751344

## Slide 12: Roller
3 sliders on bearings
5 steel panel max 500 kg each
1
2
3

## Slide 13: Roller capacity
http://www.rollon.com/GB/en/products/linear-line/

## Slide 14
Mechanical end stops
Magnetic lock (1200N) & end switch for access system

## Slide 15: Chock absorber
http://www.rossfrance.com/amortisseur_de_choc_fr.html

## Slide 16: Beam calculations IPE200
Case 1:
Load on slider 2
N

## Slide 17: Beam calculations IPE200
Case 2:
Load on slider 1 & 3
N