## Slide 1: GIF ++ ambient condition
The Prep. area outside
Tent and its gradient
CSC area
Geneva meteo station
Ian Crotty 6 Oct 2015

## Slide 2: Tent
Inside with x2 AC units
Building a tunnel across the width of the GIF++ Upstream

## Slide 3: Analogue gauges (rad hard)
Saleve T1
Front Korea T0/3
T1 Jura in front of AC
Gauges calibrated and checked to within ± 0.3degC

## Slide 4
In the beginning
Unstable data and high temps in July August 2015

## Slide 5
Temperatures 21 -30 Sept 2015
105 Supply RPC gas
203 Prep area
201 RPC tent
102 Return RPC gas
202 CSC env
Access Wednesday 23 sept 2015
Stable tent temp !

## Slide 6
CSC Temp
RPC Temp
Return RPC Gas Temp
Prep. Area Temp
Supply RPC Gas Temp
Set point change 16-18degC
The gas return temperature follows the indicated Tent temp ?

## Slide 7
Humidity RH%
201 RPC tent
102 Return RPC gas
203 Prep area
10 days

## Slide 8
Structure is perhaps due to the AC cycle 10-20mins
Humidity RH%

## Slide 9
Temp & RH in Tent & CSC
Set point change from 16deg C to 18degC and both AC on, one was off on Saleve side.
201 RPC tent
201 RPC Humidity
202 CSC Humidity
202 CSC temp.
10 days

## Slide 10
203 Prep Area RH
201 Prep Area RH
201 RPC Temp
202 Prep Area Temp
203 Prep Area RH
203 Prep Area Temp
10 days
Temp,RH & RH in Tent & CSC

## Slide 11: Conclusion
4 deg temperature gradient in the tent perhaps mostly vertical as the fans are weak. To be investigated, both inside and outside, and mitigated if confirmed.
RH values are approx. 35 – 50%
Stable 20degC values with less than 0.5degC gradient within the tent are NOT yet achieved.
RPC area is indicated as 3-4 degC less than the CSC zone.
The RPC tent is stable (±0.5) up to set point change, slow response.
Gas supply temp is higher (2degC) than Prep Area, perhaps as the gas rack are higher up.
Gas return is higher than recorded tent temp. due to gradient in height.
Gas return temperature takes the chamber temperature, to be verified.