## Sheet1
Cooling Leak tests on RE Plus 4 | [11 empty] | Ian Crotty
Data from Gerd on behalf of ZEC |  |  | EDMS doc | 1332026 | [7 empty] | 2014-01-17
[7 empty] | Volume SM | 55 |  | [litres] | [5 empty] | Vol SM
An example is ; | [15 empty] | Pipe L | 8 | [m]
| SM # | SM position | Ps | Pf | Delta P | Ts | Tf | Delta T |  | Flex pipe L | Vol Flex | Total Vol | Leak Rate | Bin Range | Frequency | Vol SM | 2.2619 | [l]
[5 empty] | [Bar] |  |  | [sec] |  | [m] | [l] | [litres] | [mbar.l/s] | [mbar.l/s]
[14 empty] | Bin | Frequency
|  | Example | 15.33 | 15.32 | 0.01 |  |  |  | 3600 | 7 | 0.39584 | 4.9197 | 0.013666
|  | Example | 15.33 | 15.32 | 0.01 | 15:32 | 16:52 | 1:20 | 4800 | 6 | 0.33929 | 4.8632 | 0.010132
|  | 13 & 14 | 15.26 | 15.24 | 0.02 | 9:20 | 10:20 | 1:00 | 3600 | 6 | 0.33929 | 4.8632 | 0.027018 | 0.001
|  | 15 & 16 | 15.52 | 15.52 | 0 | 13:20 | 14:20 | 1:00 | 3600 | 6 | 0.33929 | 4.8632 | 0 | 0.002
|  | 17 & 18 | 15.58 | 15.57 | 0.01 | 14:20 | 15:30 | 1:10 | 4200 | 6 | 0.33929 | 4.8632 | 0.011579 | 0.003
|  | 11 & 12 | 15.28 | 15.27 | 0.01 | 11:40 | 13:25 | 1:45 | 6300 | 6 | 0.33929 | 4.8632 | 0.0077193 | 0.004
|  | 9 & 10 | 15.4 | 15.38 | 0.02 | 15:00 | 16:00 | 1:00 | 3600 | 6 | 0.33929 | 4.8632 | 0.027018 | 0.005
|  | 7 & 8 | 15.29 | 15.28 | 0.01 | 10:15 | 11:25 | 1:10 | 4200 | 6 | 0.33929 | 4.8632 | 0.011579 | 0.006
|  | 3& 4 | 15.87 | 15.87 | 0 | 10:15 | 11:25 | 1:10 | 4200 | 6 | 0.33929 | 4.8632 | 0 | 0.007
|  | 5 & 6 | 15.47 | 15.44 | 0.03 | 10:55 | 13:25 | 2:30 | 9000 | 6 | 0.33929 | 4.8632 | 0.016211 | 0.008
|  | 2& 1 | 15.53 | 15.51 | 0.02 | 9:30 | 10:30 | 1:00 | 3600 | 6 | 0.33929 | 4.8632 | 0.027018 | 0.009
|  | 19 & 20 | 15.53 | 15.51 | 0.02 | 10:30 | 11:30 | 1:00 | 3600 | 2 | 0.1131 | 4.637 | 0.025761 | 0.01
|  | 21 & 22 | 15.53 | 15.51 | 0.02 | 11:30 | 12:30 | 1:00 | 3600 | 4 | 0.22619 | 4.7501 | 0.026389 | 0.011
|  | 23 & 24 | 15.53 | 15.51 | 0.02 | 12:30 | 13:30 | 1:00 | 3600 | 2 | 0.1131 | 4.637 | 0.025761 | 0.012
|  | 25 &26 | 15.53 | 15.51 | 0.02 | 13:30 | 14:30 | 1:00 | 3600 | 3 | 0.16965 | 4.6935 | 0.026075 | 0.013
|  | 27 & 28 | 15.53 | 15.51 | 0.02 | 14:30 | 15:30 | 1:00 | 3600 | 7.5 | 0.42411 | 4.948 | 0.027489 | 0.014
|  | 29 & 30 | 15.53 | 15.51 | 0.02 | 15:30 | 16:30 | 1:00 | 3600 | 5 | 0.28274 | 4.8066 | 0.026704 | 0.015
|  | 31 & 32 | 15.53 | 15.51 | 0.02 | 16:30 | 17:30 | 1:00 | 3600 | 2 | 0.1131 | 4.637 | 0.025761 | 0.016
|  | 33 & 34 | 15.53 | 15.51 | 0.02 | 17:30 | 18:30 | 1:00 | 3600 | 7.5 | 0.42411 | 4.948 | 0.027489 | 0.017
|  | 35 & 36 | 15.53 | 15.51 | 0.02 | 18:30 | 19:30 | 1:00 | 3600 | 5.5 | 0.31102 | 4.8349 | 0.026861 | 0.018
More
Comparative leak table for different parameters
|  | Delta P | Delta Time | Delta T | Volume |  | Leak Rate
|  | [mbar] | [s] |  | litres |  | [mbar.l/s]
|  | 10 | 3600 | 60 | 10 |  | 0.027778
|  | 10 | 3600 | 60 | 1 |  | 0.0027778
|  | 10 | 3600 | 60 | 0.1 |  | 0.00027778
|  | 10 | 3600 | 60 | 0.5 |  | 0.0013889
|  | 10 | 10000 | 166.6667 | 1 |  | 0.001
|  | 10 | 1000 | 16.6667 | 5 |  | 0.05 |  | Plus stability time
|  | 10 | 100 | 1.6667 | 1 |  | 0.1
|  | 10 | 10 | 0.16667 | 1 |  | 1