## Slide 1: Observation of the RPCs after UXC Set point change from 19 to 17degC
What we can observe.
Average Chamber temperatures just before and after 18 Oct 2010.
Yoke temperature.
Individual examples of chamber temps.
Distribution in Z
Longer term
Conclusions.

## Slide 2: Ambient temp change did change on the 18 Oct.
SPC = Set Point Change
19 -17 degC

## Slide 3: Average Chamber temps before SP change

## Slide 4: Average temps after SP Change
Set Point 19 -17
18 Oct 2010
0.31degC
0.28degC
0.06degC
0.36degC
0.23degC
0.04degC

## Slide 5: Observation of the RPCs after UXC Set point change from 19 to 17degC
The SPC caused the temperatures to slightly decrease, which is good.
In addition the changes were more pronounced with distance from IP.
The very small differences in the RE1s can be explained by the enclosed nature of their installation behind the CSCs.
The RE2 and 3s are greater due to the greater exposure in that the CSCs are on the opposite wall (yoke).
The difference between the RE2 and 3 may be due to the distance from the IP and associated heat sources.
It should be pointed out that absolute values differences are small.
The following slides give some individual cases

## Slide 6: Logged Yoke temps are not representative of the real conditions.
1 degC variation in less than a day
Unfortunately these logs of temperature do not allow us to improve our understanding of the actions taken and the impact on the RE system

## Slide 7: Temperature change of RE1/207. This chamber is on the YE+1
18 Oct 2010 SPC

## Slide 8: Temperature change of RE3/307. This chamber is on the YE+3
18 Oct 2010 SPC

## Slide 9: Temperature change of RE-3/307. This chamber is on the YE-3
18 Oct 2010 SPC

## Slide 10: RPC Temp Distributions in June 2010
+Z
-Z
RB0
20.33C
19.90C
19.79C
20.25C
20.25C
18.67C
19.41C
20.83C
21.33C
20.32C
21.92C
0.5C
0.8C
0.6C
0.7C
0.8C
0.75C
Gains since April 2010

## Slide 11: RPC Temp Distributions on 30 Nov 2010
+Z
-Z
RB0
20.55C
20.12C
20.05C
20.34C SD=0.28
20.57C
19.00C
19.71C SD=1.10
20.80C SD=0.4
21.58C SD=0.36
20.81C SD=0.61
22.08C SD=0.35
0.03C
0.09C
0.16C
0.25C
0.49C
0.3C
Small increases since June 2010
Mean
StDev
Increases are mitigated by the work undertaken during the year

## Slide 12: Increasing of UXC temp since Aug
Part of the reason for the increase on the long term

## Slide 13
Temperature plot of UXC for 2010
The structure is similar to the following slide showing chamber temps but without the increase since June
June to SPC

## Slide 14
RE average temperatures during 2010
Steady temp increases since June until SPC

## Slide 15
RB average temperatures during 2010
Temperatures are far more stable

## Slide 16: Observation of the RPCs after UXC Set point change from 19 to 17degC

## Slide 17: Web Based Monitoring source
RPC Temperature
Now 2010.11.30 19:20:58 UTC Heartbeat 2010.11.30 19:20:33 UTC
The green sections represent those chambers which have sensors. Clearly the RB are better instrumented than the RE.

## Slide 18: Conclusions
The Set Point Change (SPC) in the UXC reduced by 2 degrees.
The ambient temperature at the X3 level in UXC reduced by 0.6-0.8degC.
The chamber temperature reduction reached 0.3-0.4 degrees at best in the RE3 regions.
There is a persistent asymmetry in the temperatures of the RE3s.
Increases since June have been greater in the RE1s.
From June to November there has been a steady increase in RE temps that is not evident in RB.
As well as remnant heat emanating from the central detector region of CMS as has been suggested perhaps we see well cooled chambers in the barrel region and an influence of the ambient air temperature on the RE2 and RE3s. This implies that any attempt to circulate cool enough ambient air between the yokes will help.
We need a solution to keep the present RE stations as cool as the barrel and also the future RE4 that we have started building.