Tests on HV cablesfor RE4 CMS			Sergei  Lusin & iIan Crotty

Notice that there is no ground of ANY sort. See potos of test site before the incident.

27 Jan first tests to see where we are

see images 1-4

Test done with S. Lusin and his Fluka scope No XXXX

29 Jan

Now we know what we are doing ….in terms of the calibration and scope use etc

Probe is divide by 2000 NOT 1000 !!

Charging of the cables since 27 Jan at 12kV three cables, RE-4/2/34-36

Seeing 3kV over 10secs thu the probe wrt the shield, that is we have the 2 live channels (-HV) and the 0V return all “up” at 2.5-3kV of the SAME polarity. 3kV is equivalent to 3 squares of 500mV each

up with Fluke scope

See photos on my phone.

Sergei is taking notes

A short break of one hour

We are seeing a bigger range of voltages but still 2.5kV across shield  to commun  return (0V)

30 Jan. 14

It seems clear that the charge (~3kV)is on the shield and almost nothing on the conductors (x4). This could not be possible if the shield was grounded. It is also not possible that residual charge be built up as there could be no dielectric absorbtion because the shield  would be held down with the “0V” line during the charging.

Need old cable to test.

See photos of 904 Test facility before the Incident.